## Table of Contents
Customer: Earthshore | Section: Earthshore | User: Leandro Scovino
Engine Event History | Friday, April 29, 2022
Report Date Range | 7/1/2021 12:00:00 AM - 4/29/2022 12:00:00 AM
Filters Used | Filter: None
Table Of Contents | Notes
Engine Event Summary
CN - ABC00546
BE - ABC00547
BB - ABC00548
BB - ABB00239
BE - ABB00240
BE - ABB00232
BB - ABB00235
BE - ABB00230
BB - ABB00233
BE - ABB00231
BB - ABB00234
CN - ABC00574
BB - ABC00575
BE - ABC00576
DG1 - ABA00243
DG2 - ABA00133
DG3 - ABA00223
DG4 - ABA00247

## Engine Event Summary
Unit Name | High Severity Count | Medium Severity Count | Low Severity Count
BE - ABC00547 | 10 | 18 | 45
BB - ABC00548 | 10 | 15 | 48
CN - ABC00546 | 10 | 13 | 21
BE - ABC00576 | 6 | 15 | 19
DG2 - ABA00133 | 5 | 26 | 69
CN - ABC00574 | 4 | 26 | 69
BE - ABB00230 | 2 | 86 | 12
BE - ABB00231 | 1 | 87 | 12
BB - ABB00233 | 1 | 28 | 37
BB - ABC00575 | 1 | 19 | 15
DG4 - ABA00247 | 1 | 12 | 87
DG1 - ABA00243 | 1 | 4 | 14
BB - ABB00235 | 0 | 100 | 0
BE - ABB00232 | 0 | 97 | 3
BB - ABB00239 | 0 | 75 | 0
BE - ABB00240 | 0 | 52 | 0
BB - ABB00234 | 0 | 48 | 0
DG3 - ABA00223 | 0 | 4 | 96
Totals | 52 | 725 | 547

## CN - ABC00546
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2022-04-27 17:23 | 5291
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2022-04-22 11:57 | 5288
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2022-04-22 11:57 | 5288
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2022-04-22 11:57 | 5288
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2022-04-22 11:57 | 5288
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2022-04-22 11:41 | 5288
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2022-04-22 11:41 | 5288
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2022-04-22 11:40 | 5288
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-04-22 11:40 | 5288
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2022-04-22 11:35 | 5288
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-22 11:35 | 5288
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-04-22 11:33 | 5288
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-22 10:44 | 5288
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-03-07 21:19 | 5224
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 19:44 | 5224
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 17:54 | 5128
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-12-03 13:17 | 4993
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-12-03 11:47 | 4993
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2021-12-03 11:47 | 4993
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-12-03 11:47 | 4993
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-12-03 11:47 | 4993
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-12-03 11:43 | 4993
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-03 11:43 | 4993
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-12-03 11:43 | 4993
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-12-03 11:43 | 4993
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-03 11:43 | 4993
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-03 11:43 | 4993
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-02 14:49 | 4992
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-09-09 19:40 | 4929
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-09-09 19:40 | 4929
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-09-09 19:38 | 4929
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-09-09 19:38 | 4929
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-09-09 19:38 | 4929
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-09-09 19:37 | 4929
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-09-09 19:37 | 4929
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-09-09 19:37 | 4929
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-09-09 19:36 | 4929
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-09-09 19:36 | 4929
High | Event | 8:3 | Engine | High Aftercooler Temperature Shutdown | 2021-09-09 19:32 | 4929
Medium | Event | 7:2 | Engine | High Aftercooler Temperature Derate | 2021-09-09 19:32 | 4929
Low | Event | 279:1 | Engine | High Aftercooler Temperature Warning | 2021-09-09 19:32 | 4929
Low | Diagnostic | 279:3 | Engine | Aftercooler Coolant Temperature Sensor (Front):Voltage Above Normal | 2021-09-09 19:31 | 4929
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-09 14:59 | 4926
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-07-26 06:46 | 4893

## BE - ABC00547
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2022-04-22 12:21 | 34205
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2022-04-22 12:21 | 34205
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2022-04-22 12:15 | 34205
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-22 12:15 | 34205
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-04-22 12:14 | 34205
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-04-22 12:12 | 34205
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2022-04-22 12:12 | 34205
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-22 12:02 | 34205
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-24 18:18 | 33852
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 16:19 | 33814
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-24 19:14 | 33299
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-24 18:33 | 33299
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-23 10:48 | 33285
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-14 06:25 | 33126
Low | Diagnostic | 94:3 | Engine | Fuel Delivery Pressure Sensor:Voltage Above Normal | 2022-02-12 17:36 | 33092
Low | Diagnostic | 289:3 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Voltage Above Normal | 2022-02-12 17:36 | 33092
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2022-02-12 17:33 | 33092
Low | Diagnostic | 279:3 | Engine | Aftercooler Coolant Temperature Sensor (Front):Voltage Above Normal | 2022-02-12 15:20 | 33092
Low | Diagnostic | 542:3 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Above Normal | 2022-02-12 15:17 | 33092
Medium | Diagnostic | 274:3 | Engine | Atmospheric Pressure Sensor:Voltage Above Normal | 2022-02-12 14:56 | 33092
Low | Diagnostic | 175:3 | Engine | Engine Oil Temperature Sensor:Voltage Above Normal | 2022-02-12 14:38 | 33092
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2022-02-12 14:32 | 33092
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 14:32 | 33092
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2022-02-12 14:30 | 33092
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 12:46 | 33092
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-02-12 11:09 | 33090
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2022-02-12 11:09 | 33090
Low | Diagnostic | 2738:3 | Engine | Turbocharger #1 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2022-02-12 11:03 | 33090
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 10:49 | 33090
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 09:38 | 33089
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 09:36 | 33089
Low | Diagnostic | 2739:3 | Engine | Turbocharger #2 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2022-02-12 06:51 | 33088
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 06:41 | 33088
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 06:35 | 33088
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 04:37 | 33086
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 04:32 | 33086
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2022-02-12 03:22 | 33084
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-12 03:18 | 33084
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-11 21:37 | 33079
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-11 19:01 | 33076
Low | Event | 162:1 | Engine | High Boost Pressure | 2022-02-11 15:38 | 33073
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-27 23:32 | 32761
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-12-03 13:22 | 31700
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-12-03 13:22 | 31700
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-03 11:33 | 31698
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-12-03 11:33 | 31698
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-03 11:33 | 31698
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-03 11:33 | 31698
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-12-03 11:14 | 31698
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-12-03 11:14 | 31698
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-12-03 11:11 | 31698
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-12-03 11:11 | 31698
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2021-12-03 11:11 | 31698
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-12-03 11:10 | 31698
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-12-03 10:58 | 31698
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-12-03 10:58 | 31698
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-03 10:58 | 31698
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2021-12-03 10:55 | 31698
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-12-03 10:54 | 31698
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-12-03 10:50 | 31698
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-10-18 08:39 | 30936
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-18 08:15 | 30936
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-09-09 16:55 | 30240
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-09-09 16:55 | 30240
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-09-09 16:55 | 30240
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-09-09 16:55 | 30240
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-09-09 16:46 | 30240
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-09-09 16:46 | 30240
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-09-09 16:45 | 30240
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-09-09 16:45 | 30240
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-09-09 16:45 | 30240
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2021-08-21 00:24 | 29900
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-14 10:17 | 29765

## BB - ABC00548
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-28 03:07 | 24543
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-24 16:59 | 24539
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-23 06:30 | 24534
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2022-04-22 11:29 | 24515
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2022-04-22 11:29 | 24515
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2022-04-22 11:26 | 24515
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2022-04-22 11:26 | 24515
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2022-04-22 11:25 | 24515
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2022-04-22 11:25 | 24515
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2022-04-22 11:15 | 24515
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-22 11:15 | 24515
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-04-22 11:15 | 24515
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2022-04-22 10:30 | 24515
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2022-04-22 10:26 | 24515
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-04-22 10:26 | 24515
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2022-03-28 07:46 | 24153
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-24 09:20 | 24116
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-11 04:09 | 23762
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2022-01-28 22:15 | 23705
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-28 21:42 | 23704
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2022-01-28 21:40 | 23704
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2022-01-28 21:40 | 23704
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2022-01-28 21:38 | 23704
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-12-31 17:23 | 23636
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-30 09:11 | 23633
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-12-03 16:03 | 23341
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2021-12-03 16:03 | 23341
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-12-03 15:51 | 23341
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-12-03 13:15 | 23338
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-03 13:15 | 23338
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-12-03 12:04 | 23338
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-12-03 12:04 | 23338
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-03 12:02 | 23338
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-03 12:02 | 23338
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2021-12-03 12:02 | 23338
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-03 12:02 | 23273
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-12-03 12:01 | 23338
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-12-03 11:58 | 23338
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-12-03 11:57 | 23338
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2021-12-03 11:57 | 23338
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-12-03 11:55 | 23338
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-11-30 08:43 | 23272
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-11-16 08:12 | 23106
Low | Diagnostic | 175:3 | Engine | Engine Oil Temperature Sensor:Voltage Above Normal | 2021-11-16 04:16 | 23106
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-11-15 09:36 | 23106
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-11-14 10:50 | 23101
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-11-02 21:21 | 23019
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-25 03:36 | 22964
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-10-25 03:33 | 22964
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-16 05:26 | 22799
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-10 16:45 | 22770
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2021-09-09 19:30 | 22504
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2021-09-09 19:30 | 22504
High | Event | 40:3 | Engine | Low Engine Oil Pressure Shutdown | 2021-09-09 19:29 | 22504
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-09-09 19:29 | 22504
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-09-09 19:28 | 22504
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-09-09 19:27 | 22504
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-09-09 19:27 | 22504
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-09-09 19:27 | 22504
High | Event | 16:3 | Engine | High Engine Coolant Temperature Shutdown | 2021-09-09 19:26 | 22504
Medium | Event | 15:2 | Engine | High Engine Coolant Temperature Derate | 2021-09-09 19:26 | 22504
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2021-09-09 19:26 | 22504
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-09-09 19:24 | 22504
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-09 13:29 | 22504
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-09-05 10:22 | 22482
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-27 23:41 | 22383
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-27 08:02 | 22370
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-24 16:06 | 22314
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-21 00:14 | 22299
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-17 00:42 | 22290
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-08-15 03:26 | 22278
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-08-14 14:46 | 22266
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-14 10:17 | 22266

## BB - ABB00239
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 14:18 | 29234
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-25 08:42 | 29226
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-15 10:43 | 29223
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-08 10:01 | 29217
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-07 00:59 | 29213
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-29 19:47 | 29159
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-29 06:44 | 29154
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-25 15:55 | 29095
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-21 12:54 | 29094
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-19 08:39 | 29088
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-16 23:31 | 29086
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-15 18:45 | 29076
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-13 08:10 | 29066
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 06:40 | 29062
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-05 08:17 | 29059
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-27 22:38 | 29055
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 16:09 | 29004
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-24 23:06 | 28997
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-23 15:23 | 28992
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 17:41 | 28985
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 09:53 | 28980
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-21 15:11 | 28979
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 21:11 | 28978
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 14:19 | 28974
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-18 19:02 | 28970
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-18 06:53 | 28968
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-11 21:30 | 28909
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 19:20 | 28860
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-14 12:54 | 28701
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-13 07:58 | 28695
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 17:02 | 28658
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 05:38 | 28649
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-02 16:43 | 28457
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-31 11:54 | 28454
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-29 16:49 | 28437
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-24 15:36 | 28335
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-18 06:51 | 28238
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-17 15:04 | 28226
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-05 11:34 | 28002
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-29 20:04 | 27871
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-26 16:12 | 27861
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-21 21:05 | 27767
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-21 00:37 | 27764
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-19 04:46 | 27750
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-16 12:50 | 27693
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-15 11:47 | 27690
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-13 23:47 | 27670
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-01 09:33 | 27368
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-27 20:20 | 27263
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-21 12:43 | 27259
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-20 00:56 | 27253
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-19 14:18 | 27246
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-14 14:25 | 27244
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-09 16:55 | 27163
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-08 22:17 | 27159
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-05 10:08 | 27131
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-03 17:19 | 27103
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-29 15:27 | 27079
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-27 21:42 | 27077
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-23 19:48 | 27003
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-21 16:27 | 26999
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-19 23:26 | 26997
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-17 16:25 | 26981
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-14 09:47 | 26908
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-13 16:30 | 26891
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-13 06:26 | 26890
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-11 22:15 | 26867
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-07 17:31 | 26811
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-04 18:59 | 26798
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-04 14:09 | 26797
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-02 16:38 | 26794
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-01 10:40 | 26788
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-30 14:38 | 26786
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-24 10:57 | 26784
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-18 15:13 | 26647

## BE - ABB00240
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 14:20 | 30674
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-25 08:43 | 30666
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-23 12:51 | 30662
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-15 10:42 | 30659
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-12 10:50 | 30654
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-08 16:37 | 30627
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-07 01:06 | 30616
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 17:11 | 30588
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-02 09:41 | 30534
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-29 06:50 | 30519
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-21 12:58 | 30460
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-19 10:49 | 30453
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-13 08:14 | 30451
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-05 15:02 | 30447
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-05 08:19 | 30445
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-27 22:40 | 30441
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-23 15:23 | 30390
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 17:42 | 30383
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 05:26 | 30379
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-20 12:28 | 30377
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 21:11 | 30375
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 14:20 | 30372
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-18 06:56 | 30367
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-11 21:32 | 30308
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 19:21 | 30258
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-27 03:44 | 30194
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-18 15:37 | 30140
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-16 21:36 | 30115
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-16 10:40 | 30108
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-14 18:43 | 30107
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-14 13:04 | 30105
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-13 08:08 | 30098
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 19:53 | 30064
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 15:37 | 30061
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 07:54 | 30054
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-02 16:49 | 29860
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-31 12:00 | 29857
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 08:43 | 29813
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-26 09:22 | 29810
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-24 15:38 | 29788
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-21 09:16 | 29761
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-18 06:54 | 29742
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-05 11:31 | 29503
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-04 01:08 | 29485
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-29 20:04 | 29388
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-27 18:22 | 29377
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-26 16:51 | 29375
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-22 12:13 | 29280
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-21 21:20 | 29278
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-21 00:52 | 29275
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-19 05:00 | 29261
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-16 14:58 | 29204

## BE - ABB00232
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 16:09 | 55981
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 09:20 | 55978
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-26 10:23 | 55973
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-21 18:43 | 55862
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-20 12:22 | 55836
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-10 08:36 | 55592
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-08 10:38 | 55546
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 10:33 | 55481
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 17:29 | 55465
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 13:48 | 55463
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-01 10:17 | 55388
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-30 06:56 | 55370
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-28 17:40 | 55360
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-26 11:18 | 55322
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-23 15:40 | 55318
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-23 08:24 | 55311
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 16:40 | 55303
Medium | Diagnostic | 91:13 | Engine #5 | Throttle Position Sensor:Out of Calibration | 2022-03-22 14:20 | 55301
Medium | Diagnostic | 168:1 | Engine #5 | Electrical System Voltage:Low | 2022-03-22 14:20 | 55301
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 07:49 | 55301
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-21 19:32 | 55298
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-14 11:19 | 55286
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-12 16:13 | 55284
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-11 09:26 | 55254
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 22:01 | 55194
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 11:50 | 55184
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 10:36 | 55183
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-04 19:44 | 55156
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-04 10:50 | 55147
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-28 10:06 | 55125
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-24 21:01 | 55040
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-23 11:29 | 55007
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 13:10 | 54991
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 07:27 | 54989
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-20 17:13 | 54951
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-17 09:51 | 54947
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-13 11:48 | 54932
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-10 14:57 | 54930
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-05 08:03 | 54811
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 10:06 | 54789
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-31 14:49 | 54706
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-28 07:43 | 54644
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-25 08:00 | 54584
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-24 23:04 | 54581
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-20 08:08 | 54572
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-18 19:18 | 54570
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-16 00:51 | 54508
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-14 20:53 | 54480
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-13 00:13 | 54438
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-12 22:20 | 54436
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 12:50 | 54408
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-08 09:42 | 54343
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-02 22:53 | 54221
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-29 19:44 | 54122
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 18:04 | 54098
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 12:32 | 54096
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 06:40 | 54094
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-26 22:30 | 54062
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-24 17:18 | 54009
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-23 12:07 | 53979
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-18 07:37 | 53859
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-07 20:24 | 53610
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-03 23:16 | 53607
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-02 00:19 | 53567
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 20:35 | 53566
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 10:42 | 53564
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-29 23:55 | 53534
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-24 12:44 | 53406
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-20 08:38 | 53317
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-14 08:59 | 53179
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-09 15:10 | 53071
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-08 18:52 | 53061
Medium | Diagnostic | 91:8 | Engine #5 | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-11-07 14:24 | 52972
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-07 06:25 | 53036
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-04 13:18 | 52972
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-02 02:02 | 52920
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-30 03:05 | 52852
Low | Event | 48:1 | Engine #5 | Backup ECM Took Control | 2021-10-29 08:23 | 52839
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-28 17:22 | 52839
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-28 09:36 | 52837
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-23 08:13 | 52716
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-22 16:36 | 52702
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-12 04:34 | 52458
Medium | Diagnostic | 342:8 | Engine #5 | Secondary Engine Speed Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-10-11 17:12 | 52458
Low | Event | 48:1 | Engine #5 | Backup ECM Took Control | 2021-10-08 09:21 | 52458
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-07 09:19 | 52457
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-06 23:42 | 52449
Medium | Diagnostic | 276:3 | Engine #5 | Left Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 542:3 | Engine #5 | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 273:3 | Engine #5 | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 279:3 | Engine #5 | Aftercooler Coolant Temperature Sensor (Front):Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 275:3 | Engine #5 | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 289:3 | Engine #5 | Fuel Pressure Sensor - Before Fuel Filter:Voltage Above Normal | 2021-10-06 21:29 | 50158
Medium | Diagnostic | 101:3 | Engine #5 | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-10-06 21:29 | 50158
Low | Event | 48:1 | Engine #5 | Backup ECM Took Control | 2021-10-06 20:33 | 52449
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-06 20:02 | 52448
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-05 18:26 | 52428
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-04 20:34 | 52407
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 15:17 | 52363
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 11:00 | 52362

## BB - ABB00235
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 16:12 | 57145
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-27 09:20 | 57142
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-26 10:24 | 57137
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-26 04:57 | 57132
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-22 23:33 | 57055
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-20 12:26 | 57001
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-16 17:00 | 56980
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-10 08:06 | 56934
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-08 10:43 | 56932
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-07 08:43 | 56928
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 18:46 | 56920
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 08:59 | 56913
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 18:07 | 56904
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 07:02 | 56900
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-01 09:51 | 56847
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-31 16:18 | 56843
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-23 01:46 | 56637
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 08:01 | 56635
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-21 19:42 | 56632
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 08:16 | 56410
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-03 13:51 | 56341
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-23 11:29 | 56264
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 19:56 | 56250
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 13:11 | 56247
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 07:27 | 56245
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 05:54 | 56244
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-20 17:12 | 56231
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-16 18:45 | 56152
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-12 17:06 | 56054
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-06 14:48 | 56002
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-05 08:03 | 55979
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-05 05:00 | 55977
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 11:32 | 55960
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-03 09:20 | 55958
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-02 18:34 | 55953
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-02 13:52 | 55949
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-02 06:07 | 55941
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-31 13:06 | 55900
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-31 08:15 | 55898
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-28 07:45 | 55842
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-27 18:22 | 55829
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-25 08:02 | 55782
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-24 23:06 | 55780
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-22 16:30 | 55771
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-22 11:10 | 55770
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-20 08:10 | 55768
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-18 20:59 | 55766
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-16 00:52 | 55704
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-13 21:34 | 55660
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-12 23:06 | 55638
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 13:12 | 55609
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-10 10:46 | 55583
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-09 13:52 | 55563
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-08 09:48 | 55544
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-02 23:03 | 55423
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-01 09:58 | 55386
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 18:10 | 55304
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 06:36 | 55302
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-19 09:10 | 55095
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-19 01:20 | 55091
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-18 07:40 | 55084
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-17 09:09 | 55063
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-15 19:15 | 55026
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-08 19:22 | 54859
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-07 21:07 | 54838
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-03 23:14 | 54836
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-02 10:12 | 54799
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-02 00:42 | 54796
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 20:35 | 54795
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 10:30 | 54791
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-20 08:35 | 54544
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-16 18:02 | 54458
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-15 15:22 | 54431
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-14 09:00 | 54407
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-13 08:45 | 54383
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-12 12:09 | 54363
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-07 06:25 | 54251
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-05 19:31 | 54216
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-05 10:08 | 54207
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-04 13:08 | 54186
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-04 09:53 | 54183
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-31 18:32 | 54096
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-28 17:27 | 54037
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-28 09:38 | 54035
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-25 18:39 | 53975
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-25 13:12 | 53970
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-23 18:14 | 53927
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-21 15:54 | 53878
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-21 08:36 | 53872
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-14 00:13 | 53696
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-07 07:42 | 53662
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-06 20:39 | 53656
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-04 19:10 | 53608
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-03 01:45 | 53568
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 10:23 | 53565
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 04:15 | 53563
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 02:08 | 53562
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-01 00:07 | 53561
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-30 20:05 | 53558
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-06 09:39 | 52973

## BE - ABB00230
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-19 04:03 | 41697
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-19 03:47 | 41697
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-19 03:02 | 41696
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-19 02:09 | 41696
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-19 01:47 | 41695
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-19 01:06 | 41694
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-19 00:14 | 41694
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-18 23:51 | 41693
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 22:59 | 41692
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-18 22:43 | 41692
Medium | Diagnostic | 3:5 | Engine #3 | Cylinder #3 Injector:Current Below Normal | 2022-04-18 21:42 | 41691
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 21:41 | 41691
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 20:41 | 41690
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 16:57 | 41686
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 15:56 | 41685
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 14:35 | 41684
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 13:28 | 41683
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 11:13 | 41681
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 08:49 | 41678
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 06:57 | 41676
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 05:51 | 41675
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 03:56 | 41673
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-18 01:55 | 41671
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 22:42 | 41668
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 21:33 | 41667
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 20:31 | 41666
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 19:30 | 41665
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 18:16 | 41664
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 17:07 | 41662
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 15:46 | 41661
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 12:49 | 41658
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 11:38 | 41657
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-17 08:24 | 41654
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 04:57 | 41650
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-17 00:58 | 41646
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-16 22:39 | 41644
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 22:36 | 41644
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 21:22 | 41643
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 20:23 | 41642
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-16 12:55 | 41634
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-16 11:45 | 41633
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 08:35 | 41630
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 06:59 | 41628
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 05:46 | 41627
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 04:45 | 41626
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-16 03:33 | 41625
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 22:42 | 41620
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 21:39 | 41619
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-15 17:05 | 41614
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 15:39 | 41613
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 11:07 | 41608
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 07:07 | 41604
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-15 04:35 | 41602
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 04:21 | 41602
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-15 02:15 | 41600
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 01:39 | 41599
Medium | Diagnostic | 7:5 | Engine #3 | Cylinder #7 Injector:Current Below Normal | 2022-04-15 00:08 | 41597
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-14 22:56 | 41596
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-14 16:51 | 41590
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-04-14 14:43 | 41588
High | Event | 225:3 | Engine #3 | Engine Overcrank | 2022-04-14 14:43 | 41588
Medium | Diagnostic | 336:2 | Engine #3 | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2022-04-14 14:43 | 41588
Medium | Diagnostic | 444:6 | Engine #3 | Starter Motor Relay:Current Above Normal | 2022-04-14 14:43 | 41588
Medium | Diagnostic | 342:8 | Engine #3 | Secondary Engine Speed Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-04-14 14:43 | 41588
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-13 14:12 | 41588
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-10 10:12 | 41514
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-07 17:28 | 41476
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-07 09:14 | 41469
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-03 08:11 | 41385
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-02 20:49 | 41375
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-30 03:10 | 41291
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-29 09:30 | 41286
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-27 20:08 | 41277
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-27 08:35 | 41266
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-24 08:21 | 41195
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-17 22:08 | 41122
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-16 08:48 | 41100
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-15 13:18 | 41096
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-14 14:25 | 41095
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-13 08:03 | 41083
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 09:25 | 40964
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-03 10:23 | 40870
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-27 09:06 | 40819
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-26 06:32 | 40799
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 17:58 | 40787
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-24 20:23 | 40785
Medium | Diagnostic | 91:8 | Engine #3 | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-24 19:55 | 40784
Medium | Diagnostic | 542:3 | Engine #3 | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Above Normal | 2022-02-24 12:00 | 40784
Medium | Diagnostic | 100:3 | Engine #3 | Engine Oil Pressure Sensor:Voltage Above Normal | 2022-02-24 12:00 | 40784
Medium | Diagnostic | 94:3 | Engine #3 | Fuel Delivery Pressure Sensor:Voltage Above Normal | 2022-02-24 10:12 | 40775
Medium | Diagnostic | 91:13 | Engine #3 | Throttle Position Sensor:Out of Calibration | 2022-02-24 10:12 | 40775
Medium | Diagnostic | 289:3 | Engine #3 | Fuel Pressure Sensor - Before Fuel Filter:Voltage Above Normal | 2022-02-24 10:12 | 40775
Low | Event | 38:1 | Engine #3 | Low Engine Coolant Temperature Warning | 2022-02-24 10:12 | 40779
Medium | Diagnostic | 444:6 | Engine #3 | Starter Motor Relay:Current Above Normal | 2022-02-24 10:12 | 40775
Low | Event | 95:1 | Engine #3 | Fuel Filter Restriction Warning | 2022-02-24 10:12 | 40778
Medium | Diagnostic | 91:8 | Engine #3 | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-24 10:12 | 40784
High | Event | 225:3 | Engine #3 | Engine Overcrank | 2022-02-24 10:12 | 40768
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-21 12:58 | 40784
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-17 11:07 | 40780
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-16 22:48 | 40778

## BB - ABB00233
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event (J1939) | 95:15 | Not Available | Engine Fuel Filter Differential Pressure:High - least severe (1) | 2022-04-26 12:52 | 38045
Low | Event (J1939) | 95:15 | Not Available | Engine Fuel Filter Differential Pressure:High - least severe (1) | 2022-04-25 20:56 | 38029
Low | Event (J1939) | 95:15 | Not Available | Engine Fuel Filter Differential Pressure:High - least severe (1) | 2022-04-25 04:08 | 38012
Low | Event (J1939) | 102:4 | Not Available | Engine Intake Manifold #1 Pressure:Voltage Below Normal | 2022-04-23 05:46 | 37966
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-04-23 05:46 | 37966
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-23 04:34 | 37966
Low | Event (J1939) | 620:4 | Not Available | 5 Volts DC Supply:Voltage Below Normal | 2022-04-17 09:37 | 37827
Low | Event (J1939) | 110:17 | Not Available | Engine Coolant Temperature:Low - least severe (1) | 2022-04-15 09:55 | 37779
Low | Event (J1939) | 110:17 | Not Available | Engine Coolant Temperature:Low - least severe (1) | 2022-04-15 03:25 | 37773
Low | Event (J1939) | 110:17 | Not Available | Engine Coolant Temperature:Low - least severe (1) | 2022-04-15 00:18 | 37770
Low | Event (J1939) | 110:17 | Not Available | Engine Coolant Temperature:Low - least severe (1) | 2022-04-14 18:03 | 37763
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-14 11:53 | 37761
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-13 14:17 | 37760
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-11 01:24 | 37736
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-10 19:25 | 37733
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-09 15:08 | 37718
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-09 08:30 | 37714
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-08 20:03 | 37704
Low | Event (J1939) | 95:15 | Not Available | Engine Fuel Filter Differential Pressure:High - least severe (1) | 2022-04-08 08:17 | 37692
Low | Event (J1939) | 95:15 | Not Available | Engine Fuel Filter Differential Pressure:High - least severe (1) | 2022-04-07 20:55 | 37680
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 08:26 | 37668
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 08:58 | 37658
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-31 07:19 | 37584
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-30 08:17 | 37575
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-24 15:24 | 37503
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-21 08:55 | 37425
Low | Event (J1939) | 102:4 | Not Available | Engine Intake Manifold #1 Pressure:Voltage Below Normal | 2022-03-17 22:42 | 37342
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-17 15:30 | 37342
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-16 08:52 | 37326
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-14 14:29 | 37323
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-10 20:11 | 37248
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 09:32 | 37240
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-04 09:22 | 37215
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-26 22:24 | 37094
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-26 12:22 | 37084
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-26 11:33 | 37084
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-26 06:44 | 37082
High | Event (J1939) | 3671:0 | Not Available | Crank Attempt Count on Present Start Attempt:High - most severe (3) | 2022-02-26 06:38 | 37082
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 22:55 | 37082
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 18:08 | 37078
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-25 18:06 | 37078
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-25 16:17 | 37076
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 10:29 | 37076
Low | Event (J1939) | 105:3 | Not Available | Engine Intake Manifold #1 Temperature:Voltage Above Normal | 2022-02-25 10:20 | 37076
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-24 15:48 | 37075
Low | Event (J1939) | 108:4 | Not Available | Barometric Pressure:Voltage Below Normal | 2022-02-24 15:20 | 37075
Low | Event (J1939) | 101:3 | Not Available | Engine Crankcase Pressure:Voltage Above Normal | 2022-02-24 15:19 | 37075
Low | Event (J1939) | 1177:3 | Not Available | Engine Turbocharger #2 Compressor Inlet Pressure:Voltage Above Normal | 2022-02-24 15:19 | 37075
Low | Event (J1939) | 1176:3 | Not Available | Engine Turbocharger #1 Compressor Inlet Pressure:Voltage Above Normal | 2022-02-24 15:19 | 37075
Low | Event (J1939) | 108:3 | Not Available | Barometric Pressure:Voltage Above Normal | 2022-02-24 15:17 | 37075
Low | Event (J1939) | 1382:3 | Not Available | Engine Fuel Filter (suction side) Differential Pressure:Voltage Above Normal | 2022-02-24 15:16 | 37075
Low | Event (J1939) | 100:3 | Not Available | Engine Oil Pressure:Voltage Above Normal | 2022-02-24 15:16 | 37075
Low | Event (J1939) | 102:3 | Not Available | Engine Intake Manifold #1 Pressure:Voltage Above Normal | 2022-02-24 15:16 | 37075
Low | Event (J1939) | 52:3 | Not Available | Engine Intercooler Temperature:Voltage Above Normal | 2022-02-24 15:16 | 37075
Low | Event (J1939) | 94:3 | Not Available | Engine Fuel Delivery Pressure:Voltage Above Normal | 2022-02-24 15:16 | 37075
Low | Event (J1939) | 110:3 | Not Available | Engine Coolant Temperature:Voltage Above Normal | 2022-02-24 14:55 | 37075
Low | Event (J1939) | 620:4 | Not Available | 5 Volts DC Supply:Voltage Below Normal | 2022-02-24 14:55 | 37075
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-17 11:06 | 37075
Low | Event (J1939) | 620:4 | Not Available | 5 Volts DC Supply:Voltage Below Normal | 2022-02-17 09:04 | 37073
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-16 22:54 | 37073
Low | Event (J1939) | 1656:2 | Not Available | Engine Automatic Start Enable Switch:Erratic, Intermittent, or Incorrect | 2022-02-16 15:31 | 37070
Low | Event (J1939) | 620:4 | Not Available | 5 Volts DC Supply:Voltage Below Normal | 2022-02-16 15:27 | 37070
Low | Event (J1939) | 91:13 | Not Available | Accelerator Pedal Position #1:Out of Calibration | 2022-02-16 15:27 | 37070
Low | Event (J1939) | 110:3 | Not Available | Engine Coolant Temperature:Voltage Above Normal | 2022-02-16 15:12 | 37070
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-16 07:38 | 37070
Low | Event (J1939) | 620:4 | Communication Gateway #1 | 5 Volts DC Supply:Voltage Below Normal | 2022-02-11 12:50 | 36955

## BE - ABB00231
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-26 06:18 | 53078
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-21 14:46 | 53075
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-16 10:25 | 53068
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-10 14:39 | 52996
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-09 08:19 | 52972
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 16:38 | 52970
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-05 08:12 | 52968
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-03 11:35 | 52965
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-28 10:38 | 52889
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-27 15:01 | 52886
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-26 13:44 | 52883
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-25 09:18 | 52856
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 22:44 | 52852
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 15:56 | 52847
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 09:57 | 52843
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-19 17:38 | 52795
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-17 17:20 | 52792
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-17 11:19 | 52790
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-15 10:58 | 52787
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-13 21:37 | 52785
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-11 08:23 | 52730
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 18:59 | 52728
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 08:24 | 52724
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 14:59 | 52722
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-03 10:53 | 52695
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-26 10:33 | 52694
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-25 08:05 | 52672
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-23 11:54 | 52670
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 15:13 | 52648
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-16 11:49 | 52647
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-12 12:07 | 52643
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-11 08:09 | 52620
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-10 17:36 | 52617
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-08 20:32 | 52612
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-08 12:01 | 52610
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-07 20:05 | 52608
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-06 08:43 | 52606
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-01 18:20 | 52585
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-31 08:27 | 52573
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-27 09:17 | 52499
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-26 10:46 | 52495
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-25 10:03 | 52493
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-24 09:34 | 52489
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-15 15:15 | 52485
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-14 11:19 | 52461
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 17:45 | 52459
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-11 08:27 | 52457
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-09 12:08 | 52454
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-07 10:43 | 52428
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-31 09:08 | 52426
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-30 15:01 | 52408
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-30 08:19 | 52405
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 22:02 | 52403
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-28 10:30 | 52398
Medium | Diagnostic | 1249:13 | Engine #5 | Secondary Throttle Position calibration required | 2021-12-22 19:54 | 5511
Medium | Diagnostic | 337:2 | Engine #5 | Remote Emergency Stop Switch:Erratic, Intermittent, or Incorrect | 2021-12-22 19:54 | 5511
Medium | Diagnostic | 1249:8 | Engine #5 | Secondary Throttle Position signal abnormal | 2021-12-22 09:14 | 5476
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-19 12:08 | 52277
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-18 16:14 | 52271
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-17 08:18 | 52247
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-15 17:04 | 52244
Medium | Diagnostic | 261:13 | Engine #2 | Engine Timing Calibration:Out of Calibration | 2021-12-15 13:17 | 0
Medium | Diagnostic | 268:2 | Engine #2 | Programmed Parameter Fault:Erratic, Intermittent, or Incorrect | 2021-12-15 13:17 | 0
Low | Diagnostic | 276:3 | Engine | Left Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-15 13:06 | 0
Low | Diagnostic | 94:3 | Engine | Fuel Delivery Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Medium | Diagnostic | 110:3 | Engine | Engine Coolant Temperature Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Medium | Diagnostic | 273:3 | Engine | Turbocharger Outlet Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 279:4 | Engine | Aftercooler Coolant Temperature Sensor (Front):Voltage Below Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 247:9 | Engine | SAE J1939 Data Link:Abnormal Update Rate | 2021-12-15 13:06 | 0
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-15 13:06 | 0
Medium | Diagnostic | 262:4 | Engine | 5 Volt Sensor DC Power Supply:Voltage Below Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 542:3 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Above Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 100:3 | Engine | Engine Oil Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Medium | Diagnostic | 274:3 | Engine | Atmospheric Pressure Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-15 13:06 | 0
Low | Diagnostic | 175:3 | Engine | Engine Oil Temperature Sensor:Voltage Above Normal | 2021-12-15 13:06 | 0
Low | Diagnostic | 1495:2 | Engine | Injector Trim Codes Not Programmed | 2021-12-15 13:06 | 0
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2021-12-15 13:06 | 0
High | Event | 264:3 | Engine | Emergency Stop Activated | 2021-12-15 13:06 | 0
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-15 12:58 | 52242
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-13 20:58 | 52240
Medium | Diagnostic | 91:8 | Engine #5 | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-13 19:16 | 5472
Medium | Diagnostic | 1249:13 | Engine #5 | Secondary Throttle Position calibration required | 2021-12-13 16:38 | 5470
Medium | Diagnostic | 91:13 | Engine #5 | Throttle Position Sensor:Out of Calibration | 2021-12-13 16:38 | 5470
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-13 13:10 | 52237
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-13 08:46 | 52234
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-12 08:48 | 52232
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-09 10:36 | 52211
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-09 06:35 | 52208
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-03 17:14 | 52076
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-03 09:03 | 52074
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 12:48 | 52071
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-01 08:41 | 52069
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-30 10:44 | 52049
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-27 06:18 | 52021
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-24 23:45 | 52003
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-22 11:32 | 51979
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-20 15:15 | 51975

## BB - ABB00234
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-19 18:28 | 52154
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-19 08:45 | 52150
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-18 10:09 | 52147
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-18 06:57 | 52145
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-17 07:10 | 52122
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-15 12:04 | 52104
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-13 07:00 | 52099
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-08 09:41 | 51983
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-05 17:27 | 51981
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-05 08:17 | 51978
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-04 08:39 | 51975
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-03 13:14 | 51972
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 10:50 | 51950
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-30 13:44 | 51922
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-27 23:48 | 51909
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-27 10:26 | 51900
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-25 17:01 | 51899
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-24 08:21 | 51875
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-22 04:13 | 51873
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-21 08:10 | 51871
Medium | Diagnostic | 261:13 | Engine #3 | Engine Timing Calibration:Out of Calibration | 2021-09-20 16:44 | 424
Medium | Diagnostic | 542:3 | Engine #3 | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Above Normal | 2021-09-20 16:44 | 424
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-20 11:46 | 51868
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-11 14:51 | 51730
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-10 07:57 | 51709
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-08 16:53 | 51707
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-08 08:07 | 51705
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-05 08:29 | 51679
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-01 16:12 | 51654
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-31 18:12 | 51645
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-30 18:24 | 51634
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-30 07:50 | 51629
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-27 08:11 | 51565
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-24 16:52 | 51563
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-24 08:20 | 51561
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-23 17:43 | 51558
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-22 09:46 | 51556
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-20 11:17 | 51514
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-19 08:54 | 51511
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-18 07:10 | 51488
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-13 08:27 | 51377
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-10 16:41 | 51373
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-10 08:14 | 51370
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-08 08:44 | 51367
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-05 23:10 | 51333
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-02 19:47 | 51271
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-08-01 07:40 | 51235
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-07-27 07:24 | 51124

## CN - ABC00574
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-06 08:51 | 9049
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2022-04-05 15:58 | 9049
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2022-04-04 14:31 | 9049
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2022-04-04 14:31 | 9049
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-03-24 10:11 | 9049
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-03-24 10:11 | 9049
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 10:09 | 9048
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-03-11 13:51 | 9047
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-03-11 13:51 | 9047
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-10 09:27 | 9046
High | Event | 225:3 | Engine | Engine Overcrank | 2022-03-10 09:01 | 9046
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-03-09 23:16 | 9042
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-07 08:53 | 9030
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-26 05:25 | 9028
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-26 05:22 | 9028
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-26 05:22 | 9028
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2022-02-26 05:22 | 9028
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-26 03:20 | 9028
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-25 17:57 | 9026
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-22 15:27 | 9025
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-21 22:55 | 9025
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-20 16:01 | 9024
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-02-19 05:42 | 9024
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 04:53 | 9024
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-18 18:20 | 9021
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-02-18 12:00 | 9021
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-12 18:17 | 9015
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-11 09:52 | 9013
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-11 07:28 | 9012
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2022-02-09 18:15 | 8992
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-02-09 18:15 | 8992
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-07 16:23 | 8992
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-07 07:15 | 8992
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-02-07 02:59 | 8987
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2022-02-07 02:59 | 8987
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-07 00:28 | 8985
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-06 23:38 | 8984
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-06 23:38 | 8984
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-06 22:53 | 8984
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2022-02-06 21:45 | 8983
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-02-06 21:45 | 8983
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-06 21:43 | 8983
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-06 05:39 | 8983
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-06 01:17 | 8978
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-02-05 23:14 | 8976
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-05 22:28 | 8975
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-02-05 19:12 | 8974
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2022-02-05 15:32 | 8973
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-02-05 15:32 | 8973
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-02-05 15:31 | 8973
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-04 23:31 | 8961
High | Event | 225:3 | Engine | Engine Overcrank | 2022-02-04 23:26 | 8961
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2022-02-04 23:23 | 8961
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-04 23:23 | 8961
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-04 23:23 | 8961
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 20:50 | 8961
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-03 13:40 | 8946
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2022-02-03 13:38 | 8946
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-02-02 14:57 | 8938
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-01-28 20:54 | 8922
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-01-28 19:52 | 8921
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2022-01-28 15:58 | 8917
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-01-25 06:46 | 8898
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-01-25 06:46 | 8898
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2022-01-25 06:46 | 8898
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-25 05:59 | 8898
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-25 04:39 | 8897
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-25 00:59 | 8895
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 23:21 | 8894
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 21:40 | 8892
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 20:30 | 8891
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 18:22 | 8889
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 16:38 | 8887
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 15:30 | 8886
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 14:08 | 8885
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 10:07 | 8881
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-24 05:25 | 8879
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2022-01-22 11:56 | 8869
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-10 08:28 | 8833
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-14 16:42 | 8832
Low | Diagnostic | 2738:3 | Engine | Turbocharger #1 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2021-12-14 14:31 | 8832
Low | Diagnostic | 2739:3 | Engine | Turbocharger #2 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2021-12-14 14:28 | 8832
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-12-14 14:25 | 8832
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2021-12-13 12:35 | 8832
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-13 05:44 | 8829
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-13 04:19 | 8828
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2021-12-02 09:36 | 8827
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-02 08:28 | 8827
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-02 07:33 | 8826
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-12-02 07:33 | 8826
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-02 03:32 | 8826
High | Event | 13:3 | Engine | High Crankcase Pressure Shutdown | 2021-12-02 03:31 | 8826
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-11-29 19:32 | 8825
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-11-24 09:59 | 8824
Low | Diagnostic | 827:8 | Engine | Left Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-11-17 14:57 | 8823
Low | Diagnostic | 828:8 | Engine | Right Exhaust Temperature Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-11-17 14:57 | 8823
Medium | Diagnostic | 263:4 | Engine | Digital Sensor Power Supply (8V Or 12V):Voltage Below Normal | 2021-11-17 14:57 | 8823
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-17 11:59 | 8823
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2021-10-27 18:27 | 8823

## BB - ABC00575
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-04-26 15:39 | 25873
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-06 16:42 | 25604
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-04-04 19:01 | 25572
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-22 08:51 | 25367
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-15 20:17 | 25278
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2022-03-11 17:03 | 25191
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-03-11 17:03 | 25191
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-11 09:01 | 25191
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-03-11 07:12 | 25189
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2022-03-11 07:12 | 25189
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-03-11 04:11 | 25186
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2022-03-11 04:11 | 25186
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-03-08 08:52 | 25121
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-20 16:28 | 24827
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-20 16:23 | 24827
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-19 02:09 | 24789
Medium | Diagnostic | 168:1 | Engine | Electrical System Voltage:Low | 2022-02-19 01:28 | 24788
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-19 01:14 | 24788
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-10 07:47 | 24626
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-10 02:14 | 24626
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2022-02-05 00:12 | 24563
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-04 23:56 | 24617
High | Event | 225:3 | Engine | Engine Overcrank | 2022-02-04 23:50 | 24617
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2022-02-04 23:49 | 24617
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-02-04 23:49 | 24617
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-02-04 22:37 | 24616
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2022-02-04 22:07 | 24616
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-02-04 22:07 | 24616
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2022-02-04 21:29 | 24615
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2022-02-04 21:29 | 24615
Low | Event | 17:1 | Engine | High Engine Coolant Temperature Warning | 2022-02-01 16:31 | 24563
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-28 10:08 | 24488
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-13 14:45 | 24295
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-12-14 17:22 | 24000
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-17 12:23 | 23509

## BE - ABC00576
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event | 190:1 | Engine | Engine Overspeed Warning | 2022-04-04 14:44 | 27976
High | Event | 4:3 | Engine | Engine Overspeed Shutdown | 2022-04-04 14:44 | 27976
Medium | Diagnostic | 11:5 | Engine | Cylinder #11 Injector:Current Below Normal | 2022-02-19 19:23 | 27575
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-19 17:52 | 27575
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2022-02-19 17:42 | 27575
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2022-02-08 17:38 | 27460
High | Event | 13:3 | Engine | High Crankcase Pressure Shutdown | 2022-02-08 17:20 | 27460
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2022-02-08 17:00 | 27460
Medium | Event | 9:2 | Engine | High Altitude Derate | 2022-02-08 17:00 | 27460
Medium | Diagnostic | 8:6 | Engine | Cylinder #8 Injector:Current Above Normal | 2022-02-08 17:00 | 27460
Medium | Diagnostic | 6:6 | Engine | Cylinder #6 Injector:Current Above Normal | 2022-02-08 17:00 | 27460
High | Event | 264:3 | Engine | Emergency Stop Activated | 2022-02-04 14:23 | 27460
Low | Diagnostic | 2738:3 | Engine | Turbocharger #1 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2022-02-04 10:32 | 27460
Low | Diagnostic | 2739:3 | Engine | Turbocharger #2 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2022-02-04 10:32 | 27460
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2022-02-03 13:48 | 27460
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2022-02-03 13:48 | 27460
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2022-02-03 09:20 | 27460
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2022-02-03 08:30 | 27460
High | Event | 225:3 | Engine | Engine Overcrank | 2022-02-02 16:22 | 27460
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-02-02 16:18 | 27460
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-16 15:07 | 27179
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2022-01-13 14:54 | 27130
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2022-01-05 13:40 | 27014
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2021-12-21 23:12 | 26680
Low | Diagnostic | 2738:3 | Engine | Turbocharger #1 Compressor Inlet Pressure Sensor:Voltage Above Normal | 2021-12-14 15:26 | 26631
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-12-14 15:19 | 26631
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-20 10:00 | 26449
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-20 09:54 | 26449
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-17 10:37 | 26379
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-10-14 10:53 | 25913
High | Event | 225:3 | Engine | Engine Overcrank | 2021-10-14 10:23 | 25913
High | Event | 13:3 | Engine | High Crankcase Pressure Shutdown | 2021-10-14 10:18 | 25913
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-10-14 09:35 | 25913
Medium | Diagnostic | 91:8 | Engine | Throttle Position Sensor:Abnormal Frequency, Pulse Width, or Period | 2021-10-09 08:51 | 25868
Medium | Diagnostic | 6:5 | Engine | Cylinder #6 Injector:Current Below Normal | 2021-10-09 08:03 | 25868
Medium | Diagnostic | 7:5 | Engine | Cylinder #7 Injector:Current Below Normal | 2021-10-09 07:44 | 25868
Medium | Diagnostic | 9:5 | Engine | Cylinder #9 Injector:Current Below Normal | 2021-10-09 07:41 | 25868
Low | Event | 2143:1 | Engine | Low Engine Coolant Level | 2021-09-24 21:49 | 25746
Medium | Diagnostic | 10:5 | Engine | Cylinder #10 Injector:Current Below Normal | 2021-07-13 20:42 | 24743
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-07-07 10:19 | 24693

## DG1 - ABA00243
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-11-30 15:26 | 65018
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-30 15:26 | 65018
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-11-30 15:25 | 65018
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-11-26 19:13 | 64958
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-11-26 09:08 | 64897
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-08-16 14:40 | 63135
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2021-08-16 14:40 | 63158
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-08-16 14:14 | 63136
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-08-16 14:14 | 63136
Medium | Diagnostic | 16:5 | Engine | Cylinder #16 Injector:Current Below Normal | 2021-08-16 14:14 | 63109
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-08-16 14:14 | 63138
High | Event | 225:3 | Engine | Engine Overcrank | 2021-08-16 14:14 | 63138
Medium | Event | 21:2 | Engine | High Exhaust Temperature Derate | 2021-08-16 14:14 | 63121
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2021-08-16 14:14 | 63144
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-08-16 14:14 | 63158
Low | Diagnostic | 276:3 | Engine | Left Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-08-16 14:14 | 63139
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-08-16 14:14 | 63158
Low | Diagnostic | 175:3 | Engine | Engine Oil Temperature Sensor:Voltage Above Normal | 2021-08-16 14:14 | 63138
Medium | Diagnostic | 11:5 | Engine | Cylinder #11 Injector:Current Below Normal | 2021-08-16 14:14 | 63158

## DG2 - ABA00133
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-25 01:35 | 48051
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-12-19 05:02 | 47919
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-19 05:01 | 47919
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-12-18 12:23 | 47903
High | Event | 225:3 | Engine | Engine Overcrank | 2021-12-18 12:21 | 47903
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-12-12 16:58 | 47865
High | Event | 225:3 | Engine | Engine Overcrank | 2021-12-12 16:51 | 47865
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-11 10:02 | 47864
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-12-08 10:51 | 47863
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-23 14:35 | 47828
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-22 09:08 | 47824
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-11-21 09:30 | 47801
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-20 16:46 | 47784
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-16 00:42 | 47695
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-15 14:34 | 47688
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-15 10:44 | 47688
Low | Diagnostic | 101:3 | Engine | Crankcase Air Pressure Sensor:Voltage Above Normal | 2021-11-15 10:26 | 47688
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-15 00:44 | 47682
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-14 18:12 | 47679
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-14 05:49 | 47670
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-13 14:00 | 47668
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-13 05:39 | 47666
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-13 04:13 | 47665
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-13 02:52 | 47663
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-12 21:10 | 47661
High | Event | 225:3 | Engine | Engine Overcrank | 2021-11-12 20:33 | 47661
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-12 09:13 | 47661
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-11 21:36 | 47654
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-11 21:25 | 47654
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-11 12:50 | 47649
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-11 06:43 | 47646
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-11 00:43 | 47644
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-10 16:47 | 47642
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-10 06:14 | 47632
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-09 21:09 | 47631
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-09 12:38 | 47628
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-09 06:18 | 47624
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-09 00:07 | 47623
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-06 16:13 | 47571
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-06 12:21 | 47571
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-06 07:35 | 47569
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-06 07:07 | 47569
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-06 05:32 | 47569
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-05 12:34 | 47552
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-05 09:28 | 47552
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-11-05 05:00 | 47548
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-04 16:23 | 47535
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-04 14:26 | 47535
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-04 11:18 | 47532
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-04 06:42 | 47527
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-04 04:36 | 47527
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-04 00:54 | 47524
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-03 21:05 | 47523
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-03 14:07 | 47517
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-03 11:53 | 47515
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-03 09:21 | 47515
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-11-03 08:24 | 47514
Low | Event | 100:1 | Engine | Low Engine Oil Pressure Warning | 2021-11-02 21:30 | 47513
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-01 08:28 | 47494
High | Event | 225:3 | Engine | Engine Overcrank | 2021-10-29 18:34 | 47478
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-29 16:18 | 47478
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-27 04:51 | 47430
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-10-26 17:22 | 47418
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-25 06:35 | 47394
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-23 11:43 | 47361
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-23 03:57 | 47356
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-21 03:10 | 47330
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-20 11:04 | 47315
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-18 22:48 | 47297
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-18 14:03 | 47295
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-15 11:01 | 47257
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-14 16:55 | 47256
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-10-14 14:42 | 47253
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-11 21:45 | 47188
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-11 17:18 | 47187
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-10 18:32 | 47183
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-10 03:52 | 47172
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-08 07:40 | 47167
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-08 02:58 | 47167
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-05 20:59 | 47124
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-05 19:43 | 47124
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-05 12:04 | 47119
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-10-04 18:16 | 47101
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-04 17:26 | 47101
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-01 10:53 | 47031
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-09-28 19:14 | 46970
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-09-26 15:03 | 46922
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-21 22:32 | 46821
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-09-21 02:34 | 46812
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-20 14:27 | 46812
High | Event | 198:3 | Engine | Low Fuel Pressure | 2021-09-19 02:31 | 46777
Low | Diagnostic | 289:3 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Voltage Above Normal | 2021-09-19 02:31 | 46777
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-09-19 02:30 | 46777
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-09-11 12:19 | 46735
Low | Diagnostic | 105:3 | Engine | Inlet Manifold Temperature Sensor:Voltage Above Normal | 2021-09-07 16:39 | 46732
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-07 13:54 | 46732
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-06 02:29 | 46713
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-09-05 23:14 | 46711
Medium | Diagnostic | 10:5 | Engine | Cylinder #10 Injector:Current Below Normal | 2021-09-03 17:06 | 46671
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-09-03 05:49 | 46671

## DG3 - ABA00223
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2022-01-01 11:45 | 59324
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2022-01-01 10:47 | 59323
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2022-01-01 10:47 | 59323
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 22:38 | 59323
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 21:36 | 59322
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 20:24 | 59320
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 18:18 | 59318
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 17:13 | 59317
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 16:08 | 59316
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-12-30 14:39 | 59315
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-30 14:01 | 59314
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 11:49 | 59313
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-30 06:35 | 59308
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-12-30 01:09 | 59303
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 23:29 | 59301
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 21:41 | 59299
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 19:53 | 59297
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 18:02 | 59296
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 15:27 | 59293
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 14:07 | 59292
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-29 10:17 | 59288
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2021-12-26 02:16 | 59213
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2021-12-26 02:16 | 59213
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-26 01:04 | 59211
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-12-25 05:22 | 59202
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-12-25 01:57 | 59199
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-23 08:24 | 59171
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-23 08:24 | 59171
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-12-23 08:23 | 59171
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-22 09:09 | 59153
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-22 09:09 | 59153
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-12-22 09:09 | 59153
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-12-21 06:05 | 59132
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-12-21 04:17 | 59131
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-21 03:42 | 59130
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-21 03:42 | 59130
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-12-21 03:42 | 59130
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-20 06:51 | 59122
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-20 06:51 | 59122
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-18 18:38 | 59117
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-18 14:17 | 59116
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-18 14:17 | 59116
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-17 14:43 | 59105
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-17 14:43 | 59105
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-17 07:46 | 59098
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-14 04:10 | 59098
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-13 16:42 | 59096
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-13 16:42 | 59096
Low | Diagnostic | 542:4 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Voltage Below Normal | 2021-12-13 16:42 | 59096
Low | Event | 101:1 | Engine | High Crankcase Pressure Warning | 2021-12-13 15:43 | 59095
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-11 12:51 | 59093
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-11 12:51 | 59093
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-12-08 11:02 | 59069
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2021-12-08 10:52 | 59069
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2021-12-08 10:52 | 59069
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-08 09:25 | 59069
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-08 08:13 | 59068
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-08 07:25 | 59067
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-08 06:23 | 59066
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-08 02:50 | 59062
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-08 01:49 | 59061
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-08 00:48 | 59060
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 23:47 | 59059
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 22:45 | 59058
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 20:58 | 59056
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 19:43 | 59055
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 18:08 | 59053
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 16:03 | 59051
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 15:01 | 59050
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 13:45 | 59049
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-07 12:38 | 59048
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-07 08:48 | 59044
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2021-12-07 07:42 | 59043
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-07 01:38 | 59043
Low | Diagnostic | 276:3 | Engine | Left Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-06 23:24 | 59043
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-06 15:38 | 59035
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-06 14:16 | 59034
Low | Event | 272:1 | Engine | Inlet Air Restriction Warning | 2021-12-06 14:00 | 59034
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-03 06:25 | 59033
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-03 04:56 | 59031
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-03 03:53 | 59030
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-03 01:50 | 59028
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-03 00:35 | 59027
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 23:31 | 59026
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 22:26 | 59025
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 21:07 | 59024
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 12:37 | 59015
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-02 07:38 | 59010
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-02 06:21 | 59009
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-02 05:07 | 59008
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 04:06 | 59006
Low | Diagnostic | 275:3 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Above Normal | 2021-12-02 04:04 | 59006
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 02:20 | 59005
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-02 01:20 | 59004
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 23:41 | 59002
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 22:24 | 59001
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 19:53 | 58998
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 17:40 | 58996
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 16:37 | 58995
Low | Diagnostic | 275:4 | Engine | Right Turbocharger Inlet Pressure Sensor:Voltage Below Normal | 2021-12-01 15:36 | 58994

## DG4 - ABA00247
Severity | Type | Code | Source | Description | Sample Time | Run Hours
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-31 05:31 | 53892
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-31 05:31 | 53892
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-30 14:12 | 53883
Low | Diagnostic | 542:2 | Engine | Engine Oil Pressure Sensor - Before Oil Filter:Erratic, Intermittent, or Incorrect | 2021-12-29 07:42 | 53858
Low | Diagnostic | 100:2 | Engine | Engine Oil Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-29 07:42 | 53858
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-29 01:52 | 53856
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-26 00:39 | 53806
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-25 06:44 | 53804
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-12-25 00:47 | 53799
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-24 23:13 | 53799
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-12-24 20:16 | 53799
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-24 16:26 | 53795
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-12-24 08:42 | 53795
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-24 06:40 | 53793
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-12-23 07:31 | 53786
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-12-23 07:19 | 53786
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-12-23 07:18 | 53786
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-12-21 04:19 | 53759
Low | Diagnostic | 289:3 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Voltage Above Normal | 2021-12-08 11:26 | 53690
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-12-08 10:01 | 53690
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-12-06 14:02 | 53690
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-12-06 14:02 | 53690
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-30 19:28 | 53614
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-30 19:28 | 53614
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-30 10:45 | 53565
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-11-28 11:19 | 53609
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-21 08:23 | 53574
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-21 07:20 | 53573
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-20 20:31 | 53572
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-20 20:31 | 53572
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-20 12:54 | 53565
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-20 04:18 | 53565
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-11-18 06:05 | 53542
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-17 10:35 | 53525
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-17 10:35 | 53525
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-16 21:20 | 53512
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-16 10:47 | 53505
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-16 10:47 | 53505
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-16 09:50 | 53504
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-16 08:40 | 53503
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-11-16 05:20 | 53502
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-16 04:46 | 53501
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-16 01:06 | 53501
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-15 21:04 | 53500
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-15 21:04 | 53500
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-15 19:18 | 53498
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-15 18:16 | 53498
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-15 18:16 | 53498
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-15 10:07 | 53495
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-15 10:07 | 53495
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-15 07:27 | 53493
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-15 06:26 | 53492
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-11-15 03:05 | 53491
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-11-15 03:05 | 53491
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-14 06:23 | 53474
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-11-13 23:02 | 53474
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-13 21:13 | 53474
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-13 05:57 | 53459
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-13 04:44 | 53457
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-13 02:29 | 53455
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-13 01:25 | 53454
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-13 00:24 | 53453
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-12 23:13 | 53452
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-12 22:03 | 53451
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-11 13:27 | 53438
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-11-10 18:45 | 53432
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-11-10 16:07 | 53431
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-11-03 12:36 | 53311
Low | Diagnostic | 94:2 | Engine | Fuel Delivery Pressure Sensor:Erratic, Intermittent, or Incorrect | 2021-10-30 13:06 | 53306
Low | Diagnostic | 289:2 | Engine | Fuel Pressure Sensor - Before Fuel Filter:Erratic, Intermittent, or Incorrect | 2021-10-30 13:06 | 53306
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-30 05:59 | 53303
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-30 03:46 | 53302
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-27 08:33 | 53248
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-27 06:12 | 53247
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-25 07:13 | 53215
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-24 20:23 | 53208
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-21 15:37 | 53175
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-21 14:49 | 53174
Low | Event | 95:1 | Engine | Fuel Filter Restriction Warning | 2021-10-21 14:08 | 53174
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-19 08:03 | 53143
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-19 01:59 | 53140
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-18 22:42 | 53140
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-17 01:26 | 53130
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-17 01:10 | 53130
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-17 01:03 | 53130
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-16 20:18 | 53127
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-16 20:04 | 53127
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-15 17:46 | 53109
High | Event | 225:3 | Engine | Engine Overcrank | 2021-10-15 17:28 | 53109
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-14 17:10 | 53092
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-12 23:01 | 53092
Low | Event | 99:1 | Engine | Engine Oil Filter Restriction Warning | 2021-10-10 11:24 | 53032
Medium | Event | 9:2 | Engine | High Altitude Derate | 2021-10-05 10:08 | 52946
Medium | Event | 9:2 | Engine | High Altitude Derate | 2021-10-05 03:00 | 52939
Low | Diagnostic | 336:2 | Engine | Engine Control Switch:Erratic, Intermittent, or Incorrect | 2021-10-03 11:35 | 52911
Low | Event | 173:1 | Engine | High Exhaust Temperature Warning | 2021-10-02 14:34 | 52892
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-02 14:03 | 52891
Medium | Diagnostic | 590:9 | Communication Gateway #1 | Engine Control Module:Abnormal Update Rate | 2021-10-02 13:36 | 52891
Low | Event | 38:1 | Engine | Low Engine Coolant Temperature Warning | 2021-10-02 05:38 | 52883
Medium | Event | 31:2 | Engine | Air Filter Restriction Derate | 2021-10-02 05:29 | 52883